## Slide 1: 2021 Adequacy Assessment Status Report
Resource Adequacy Advisory Committee
Technical Committee Webinar
April 21, 2016
1:30 to 4:00

## Slide 2: Agenda
Review of reference case and other scenarios
Preliminary results (if available)
Detailed discussion of load forecasts
  Brief description of Long and Short-term Models
  Comparison of LTM and STM loads
  Adding hourly load shapes and EE savings to the LTM (load stretching program)
Description of load stretching program, if time and interest allow

## Slide 3: 2021 Reference Case (see next slide for more detail)
Loads (from 7th power plan)
  Long-term model frozen-efficiency medium loads
  EE quarterly mean and peak targets from 7th plan
  Hourly loads derived from short-term model (load stretching)
  Existing DR (?)
Import availability
  Spot (available all hours, winter only)
  Purchase Ahead (available light-load hours, all year)
IPP generation
  Full availability (2,943 MW) winter
  Limited availability (1,000 MW) summer
Wind 4,845 MW nameplate (modeled as BPA wind) (?)
Solar 248 MW nameplate, fixed generation pattern (?)

## Slide 4: Reference Case Assumptions
Item | Quarter 4 | Quarter 1 | Quarter 2 | Quarter 3
Mean Load1 (aMW) | 22,059 | 22,263 | 19,962 | 20,837
Peak Load1 (MW) | 31,191 | 31,733 | 25,022 | 26,448
DSI Load (aMW) | 338 | 338 | 338 | 338
Mean EE (aMW) | 1,545 | 1,574 | 1,274 | 1,208
Peak EE (MW) | 2,660 | 2,660 | 1,680 | 1,680
Existing DR (MW) (?) | 607 | 607 | 1,047 | 1,047
Spot Imports (MW) | 2,500 | 2,500 | 0 | 0
Purchase Ahead (MW) | 3,000 | 3,000 | 3,000 | 3,000
1No EE or DSI

## Slide 5: Suggested Scenarios
Reference Studies (for heat map)
  Reference Case (see previous slides)
  Load Ranges (medium and high) (?)
  Import Ranges (1700, 2500, 3400 MW) (?)
Sensitivity Studies
  Reference Case using STM loads
  Fuel Limitation Case
    Reduce IPP winter capacity by about 20% (roughly 600 MW) (?)
    Potential future enhancement – IPP winter capacity as a function of temperature
  Demand Response Sensitivity
    No DR
    Minimum DR (existing DR + 600 MW from RPM)
    Expected DR (existing DR + 1,300 MW from RPM)

## Slide 6: Not Modeled for 2021
Import uncertainty
  Forced outage rate for intertie
  “Forced outage” rate for imports
Market friction
  Mostly focused on within region exchanges
  Because of nodal structure in GENESYS cannot do explicitly
  Can vary in-region market as function of temperature as a surrogate approach
Model economic load uncertainty explicitly
  Instead of high and low load scenarios
  Built in as a random variable

## Slide 7: 2021 Preliminary Results NOT FOR GENERAL DISTRIBUTION
Study | No DR | Exist DR | Min DR | Expected DR
7th Plan Med LTM (no EE) | 16 | 12 | 9 | 7
7th Plan Low LTM (no EE) | 6 | 4 | 3 | 2
7th Plan High LTM (no EE) | 37 | 28 | 21 | 16

## Slide 8: 2021 Preliminary Results NOT FOR GENERAL DISTRIBUTION
Study | No DR | Exist DR | Min DR | Exp’d DR
7th Plan Med LTM (no EE) | 16 | 12 | 9 | 7
7th Plan Low LTM (no EE) | 6 | 4 | 3 | 2
7th Plan High LTM (no EE) | 37 | 28 | 21 | 16
Med STM (implicit EE) | 11.3 | 10.2 | 9.4 | 8.1
Med LTM Hybrid Mo EE | 12.5 | 8.8 | 6.4 | 4.6
Preferred method is LTM Hybrid approach using monthly shaped EE targets.
In the med load scenario, the region needs all 1,400 aMW of EE and 1,300 MW of demand response to get below 5% LOLP.