## Slide 1: Power Supply Adequacy for the 2021 Operating Year
Resource Adequacy Advisory Committee
Steering Committee Webinar
June 8, 2016

## Slide 2: 2021 Reference and Sensitivity Cases

## Slide 3: 2021 Reference Case (see next 3 slides for more detail)
Loads (from long-term model hybrid method)
  Long-term model weather-normalized frozen-efficiency monthly loads
  Add weather-normalized daily and hourly shapes
  Add 7th plan EE targets by applying monthly effects
  Add temperature variations from short-term model
Demand Response: Existing + 121 MW planned DR
Import availability
  Spot (available all hours, winter only)
  Purchase Ahead (available light-load hours, all year)
IPP generation
  Full availability (2,943 MW) winter
  Limited availability (1,000 MW) summer
Wind 4,896 MW nameplate (modeled as Columbia Gorge wind)
Solar 396 MW nameplate, fixed generation pattern

## Slide 4: Reference Case Assumptions
Item | Quarter 4 | Quarter 1 | Quarter 2 | Quarter 3
Mean Load (aMW) | 21,234 | 20,975 | 18,813 | 19,987
Peak Load (MW) | 33,768 | 33,848 | 26,504 | 28,302
DSI Load2 (aMW) | 338 | 338 | 338 | 338
Mean EE (aMW) | 1,545 | 1,574 | 1,274 | 1,208
Peak EE (MW) | 2,660 | 2,660 | 1,680 | 1,680
Spot Imports (MW) | 2,500 | 2,500 | 0 | 0
Purchase Ahead (MW) | 3,000 | 3,000 | 3,000 | 3,000
2DSI load is 338 aMW in low, med and high load cases in 2021.

## Slide 5: Example of Energy Efficiency Savings 2021 Hybrid Loads January (1929 Temp)
Average On-Peak Savings = 1,736 MW-Weeks
Average Off-Peak Savings = 1,097 MW-Weeks
Average Weekly Savings = 1,416 MW-Weeks

## Slide 6: Scenarios
Reference Studies (for heat map)
  Reference Case (see previous slides)
  Load Ranges (low, medium and high)
  Import Ranges (1700, 2500, 3400 MW)
Sensitivity Studies
  Reference Case using STM loads
  Fuel Limitation Case: Reduce winter gas IPP capability by 35% (650 MW), reduces all-fuel winter IPP cap by 22%
    Reduces winter IPP total cap from 2943 to 2293 MW
    Reduces summer IPP total cap from 1000 to 779 MW
  Standby Resource Sensitivity
    Existing + Planned DR and Emergency Generation
    Existing + Planned + RPM Minimum DR (500 MW)
    Existing + Planned + RPM Expected DR (1,257 MW)

## Slide 7: 2021 Adequacy Assessment

## Slide 8: 2021 Power Supply Adequacy
10% LOLP = Inadequate Supply (medium case)
  Counting existing and expected resources only, and
  Seventh plan EE targets, and
  Existing + 121 MW of planned DR + standby generation
Primarily capacity short – 1,040 to 2,230 MW of new capacity needed (for medium and high load growth cases)
Seventh power plan resource strategy should be used for resource acquisition plans.
Part of needed capacity can come from demand response. Any amount of new DR will increase adequacy.

## Slide 9: Comparison to last year’s 2021 Assessment (from 8.3 to 9.9% LOLP)
2021 Annual Load:
  Last year’s forecast 21,780 aMW
  Current forecast1 20,250 aMW (range 19,580 to 20,900)
  Net decrease - 1,530 aMW
2021 Average Winter Peak Load:2
  Last year’s forecast 30,865 MW
  Current forecast 33,848 MW
  Net increase 2,983 MW
Resources
  Small amount of new solar capacity
  Up to 2,000 MW less hydro peaking (from BPA-only to regional INC/DEC)
Newer version of GENESYS (tends to show slightly higher LOLP)
1Load forecasting method was modified for a more accurate reflection of energy efficiency savings and the impacts of future codes and standards.
2Even though the current annual average load forecast for 2021 is lower than last year’s, this year’s winter peak load forecast is much higher. Council will continue to investigate this and also why off-peak loads in this year’s forecast appear to be lower than expected.
Main reasons why LOLP is higher in this year’s assessment

## Slide 10: Comparison to Past Assessments
Year Analyzed | Operation Year | LOLP | Observations
2010 | 2015 | 5% | Was part of the Council’s 6th Power Plan
2012 | 2017 | 7% | Imports deceased from 3,200 to 1,700 MW, load growth 150 aMW per year, only 114 MW of new thermal capacity
2014 | 2019 | 6% | Load growth 0.6%, over 600 MW new generating capacity, increased imports by 800 MW
2015 | 2020 | 5% | Lower load forecast, 350 MW of additional EE savings
2015 | 2021 | 8.3% | Early estimate (BPA INC/DEC only) Loss of Boardman and Centralia 1 (~1,330 MW)
2016 | 2021 | 10% | 2021 loads lower than last year’s forecast (~1,500 aMW) but winter peaks are higher (~3,000 MW), using regional INC/DEC reduces hydro peaking by as much as 2,000 MW

## Slide 11: Sensitivity Studies

## Slide 12: LOLP (%) Heat Map (existing standby resources)
10
12
8
24
4
22
26
2
6
3400
2500
1700
High
Med
Low
Imports
Loads
Let’s examine the effects of adding DR to the reference case.

## Slide 13: Effects of DR on LOLP (2500 MW import)
Standby Loads | Exist | + Minimum RPM DR | + Average RPM DR
High Load | 24 | 19 | 10
Med Load | 10 | 8 | 5
Low Load | 4 | 3 | 2

## Slide 14: Loss of Gas/Market Friction (Loss of 650 MW IPP, 2500 MW import)
Standby Loads | Ref Case | Existing DR | + Minimum RPM DR | + Average RPM DR
High Load | 24 | 30 | 23 | 13
Med Load | 10 | 13 | 10 | 6
Low Load | 4 | 6 | 5 | 3

## Slide 15: Other Adequacy Metrics

## Slide 16: EUE (MW-hours) (existing standby resources)
Imports Loads | 3,400 | 2,500 | 1,700
High Load | 6,400 | 8,700 | 11,800
Med Load | 1,200 | 2,500 | 3,000
Low Load | 200 | 700 | 1,600

## Slide 17: Effects of DR on EUE (2500 MW import)
Standby Loads | Exist | + Minimum RPM DR | + Average RPM DR
High Load | 8,700 | 6,400 | 4,100
Med Load | 2,500 | 1,800 | 900
Low Load | 700 | 500 | 200

## Slide 18: Expected Hours Curtailed (hours) (existing standby resources) (Green satisfies 1-in-10 year criterion of 1.1 max)
Imports Loads | 3,400 | 2,500 | 1,700
High Load | 8.2 | 9.4 | 10.7
Med Load | 1.6 | 2.4 | 3.1
Low Load | 0.3 | 0.7 | 1.3

## Slide 19: CVaR Peak (MW) (existing standby resources)
Imports Loads | 3,400 | 2,500 | 1,700
High Load | 2,513 | 3,293 | 4,178
Med Load | 1,374 | 2,1851 | 3,045
Low Load | 302 | 909 | 1,831
1Implies a 1,145 MW threshold for a 5% LOLP (2,185 – 1,040 needed for 5%).

## Slide 20: Historical vs. Forecast Loads
Why do the 2021 forecasted hourly loads look peakier than historic hourly loads?
Historic loads based on 1993 to 2014 record
Forecasted loads use 1929-05 temperatures
Historic load period misses some extreme temperature years (e.g. 1950)
When same period is used, forecasted loads are not peakier
Minimum hourly loads seem to be too low but peak and average loads seem alright

## Slide 21: Winter Max Load Hour Historical (’93-’05) vs. Hybrid Forecast (’29-’05)

## Slide 22: Summer Max Load Hour Historical (’93-’05) vs. Hybrid Forecast (’29-’05)

## Slide 23: Max Historic (93-05) vs Max Forecast (29-05) Week 14

## Slide 24: Max Historic (93-05) vs Max Forecast (93-05) Week 14

## Slide 25: Max Historic (93-05) vs Max Forecast (29-05) Week 17

## Slide 26: Max Historic (93-05) vs Max Forecast (93-05) Week 17

## Slide 27: Additional Slides

## Slide 28: Curtailment Statistics (before standby resources)
6160 = number of simulations (years)
838 = number of event years
13.6 % = LOLP (9.9% after standby resources applied)
2374 = total number of events
11.1 hours = average event duration
2,704 MW-hours = average event magnitude
1,183 MW = average event peak outage
2.6 = expected number of events/year (over all years)
4.3 hours = expected hours curtailed/year (over all years)